600 kW Industrial Water Heating System with Grid-Tied PV Offset

Faculty of Mechanical Engineering, GIK Institute
Date: June 29, 2025

### 1. Objective

To design and estimate a 600 kW industrial water heating system with a grid-tied solar photovoltaic (PV) system capable of offsetting the 24/7 electrical demand through net metering, without the use of batteries.

### 2. Part A: Industrial Water Heating System Design

#### 2.1 Heating Requirements

Based on the attached energy calculations (see Section 2 of original document), the total thermal energy required to heat and maintain the 12-ton water tank is:

- Steady-State Heating Requirement: 576.2 kW

- Tank Maintenance Load: 586.9 kW

- Design Basis: System is rated for 600 kW total power.

#### 2.2 Suitable Heater Types

| Type of Heater | Suitable for | Power Range | Pros | Cons |
| --- | --- | --- | --- | --- |
| Flanged Immersion | Industrial tanks | 20–1000+ kW | High capacity, easy maintenance | Requires tank flange |
| Screw-Plug Immersion | Smaller modular installs | 1–60 kW | Compact, cheap | Requires many units and ports |
| Circulation (Inline) | With pumping loop | Up to 500 kW each | External mounting, serviceable | Requires pump, piping |

Recommended Type: Flanged Immersion Heaters (Incoloy 800/825 or SS316 sheath), 10x60 kW or 6x100 kW configuration.

#### 2.3 Supplier Estimates

Pakistan:

- Thermotech (Karachi): 10×60 kW flanged immersion heaters, Incoloy 825 sheaths: PKR 0.8–1.0 million/unit, total: PKR 8–10 million

- Naeem Engineering: 6×100 kW flanged heaters, SS304 flanges and Incoloy elements: PKR 1.1–1.2 million/unit, total: PKR 6.6–7.2 million

USA:

- Chromalox: Custom 60 kW flanged units, SS or Incoloy elements: $3,500–4,000 each, total: $35,000–40,000

- Watlow: 60–100 kW WATROD® flanged units: $2,800–4,500 each, total: $35,000–45,000

#### 2.4 Summary Recommendation

- Use flanged immersion heaters for durability and serviceability.

- Material: Incoloy 800/825 or SS316 to tolerate industrial water.

- Mounting: ANSI flanged ports to be welded to tank wall.

- Power Distribution: 10×60 kW or 6×100 kW units.

### 3. Part B: Grid-Tied PV System to Offset 600 kW Load (24/7)

#### 3.1 Objective

Offset a continuous 600 kW electrical heating load (14,400 kWh/day) using solar PV, without battery storage. Surplus daytime generation will be net-metered against nighttime grid consumption.

#### 3.2 Solar Irradiance & Yield

- Location: Swabi District, KP, Pakistan

- Average Solar Irradiance: ~5.8–6.0 kWh/m²/day

- System Efficiency: ~75–80%

- Daily PV Output Target: 14,400 kWh

#### 3.3 PV System Sizing

| Parameter | Value |
| --- | --- |
| Daily energy need | 14,400 kWh |
| Effective sun hours | 6.0 kWh/kW-day |
| System efficiency | 75–80% |
| Required PV capacity | 3.2 to 3.3 MW (DC) |
| Module size | 540–600 W (mono PERC) |
| Number of panels | ~5,500–6,000 |
| Land required | ~15 acres (≈6 hectares) |

#### 3.4 Inverter and Mounting System

- Inverters: 2×1.65 MW central or 10×330 kW string inverters

- Mounting: Fixed ground-mount with 30° south-facing tilt

#### 3.5 Cost Estimate (Exchange rate: 1 USD = PKR 285)

| Item | Cost (PKR) | Cost (USD) |
| --- | --- | --- |
| PV Modules (6000×600W) | 122,400,000 | $429,000 |
| Inverters | 50,000,000 | $175,000 |
| Racking & Mounting | 80,000,000 | $280,000 |
| Cabling & Combiner Boxes | 30,000,000 | $105,000 |
| Civil Works & Labor | 50,000,000 | $175,000 |
| Grid-Tie Infrastructure | 20,000,000 | $70,000 |
| Contingency (15–20%) | 67,600,000 | $236,000 |
| Total Estimate | ~420,000,000 | ~$1.47M |

#### 3.6 Financial Feasibility

- Levelized Cost of Electricity (LCOE): Rs 5–9/kWh

- Offset Tariff: Rs 30–35/kWh (Industrial grid rate)

- Simple Payback: ~2–3 years

- ROI over 25 years: Very High (>100%)

#### 3.7 Final PV System Summary

- Design: Grid-tied, net-metered, ground-mounted

- Capacity: 3.3 MW to offset 600 kW continuous load

- Panels: 540–600 W mono PERC, ~6,000 units

- Total Cost: Rs. 420–600 million (USD 1.47–2.1M)

### 4. Conclusion

The combined industrial heating and PV offset solution integrates:

- A durable flanged-immersion electric heating system rated for 600 kW.

- A grid-tied 3.3 MW PV system to offset full daily electrical demand via net metering.

This system provides a sustainable, low-LCOE, and highly efficient thermal energy supply solution for industrial applications, with rapid return on investment and scalability for future integration.

### 5. References

- Chromalox Product Catalog, www.chromalox.com

- Watlow Heater Selection Guide, www.watlow.com

- Thermotech Pakistan, www.thermotech.com.pk

- Pakistan Meteorological Department, Solar Resource Data

- SolarGIS / PVGIS Database, EU Commission

- NEPRA Tariff Determination Reports (2023–2025)

- NREL PVWatts Calculator, https://pvwatts.nrel.gov

- “Photovoltaic System Design Handbook” – J. N. Stone, CRC Press

- Industrial Heating Elements Guide – Wattco, www.wattco.com

- ASHRAE Handbook of HVAC Systems and Equipment